## 315kVA (hidden)
Rating | 315kVA
Wilson e1 ECO Tier 1 |  |  |  | Wilson e2 ECO Amorphous Tier 2
Basic Ex works price in £s |  | 7550 |  | Basic Ex works price in £s | 9995
No Load Loss in Watts (NLL) |  | 360 |  | No Load Loss in Watts (NLL) | 200
Load Loss in Watts (LL) |  | 3900 |  | Load Loss in Watts (LL) | 2800
Additional investment in Wilson e2 ECO Amorphous Super Low Loss in £s |  |  |  |  | 2445
NLL Saved Watts | LL Saved Watts | Annual Savings
|  | Due to No Load Losses | Considering Load factor of (xx)% | Total kWh | CO2 Reduced (t)
|  |  | 70 |  | (GEF=0.537)
160 | 1100 | 1401.6 | 4721.64 | 6123.24 | 3.2882
No of Years | Extra Investment on Wilson e2 | Energy Cost in £s (per kWh) (Increasing 2.0% per annum) | Cost of energy saved for kWh/year | Extra Investment carried forward | Remarks
0 | 2445
1 | 1771.3336 | 0.11 | 673.5564 | 1771.3336 | Payback Period
2 | 1084.1939 | 0.1122 | 687.0275 | 1084.1939 | Payback Period
3 | 383.3113 | 0.11444 | 700.7681 | 383.3113 | Payback Period
4 | -331.5888 | 0.11673 | 714.7834 | -331.5888 | Lifetime Savings
5 | -1060.787 | 0.11907 | 729.0791 | -1060.787 | Lifetime Savings
6 | -1804.5691 | 0.12145 | 743.6607 | -1804.5691 | Lifetime Savings
7 | -2563.2269 | 0.12388 | 758.5339 | -2563.2269 | Lifetime Savings
8 | -3337.0579 | 0.12636 | 773.7046 | -3337.0579 | Lifetime Savings
9 | -4126.3654 | 0.12888 | 789.1787 | -4126.3654 | Lifetime Savings
10 | -4931.4591 | 0.13146 | 804.9622 | -4931.4591 | Lifetime Savings
11 | -5752.6547 | 0.13409 | 821.0615 | -5752.6547 | Lifetime Savings
12 | -6590.2742 | 0.13677 | 837.4827 | -6590.2742 | Lifetime Savings
13 | -7444.6461 | 0.13951 | 854.2324 | -7444.6461 | Lifetime Savings
14 | -8316.1054 | 0.1423 | 871.317 | -8316.1054 | Lifetime Savings
15 | -9204.9939 | 0.14514 | 888.7434 | -9204.9939 | Lifetime Savings
16 | -10111.6602 | 0.14805 | 906.5182 | -10111.6602 | Lifetime Savings
17 | -11036.4598 | 0.15101 | 924.6486 | -11036.4598 | Lifetime Savings
18 | -11979.7554 | 0.15403 | 943.1416 | -11979.7554 | Lifetime Savings
19 | -12941.9169 | 0.15711 | 962.0044 | -12941.9169 | Lifetime Savings
20 | -13923.3216 | 0.16025 | 981.2445 | -13923.3216 | Lifetime Savings
21 | -14924.3545 | 0.16345 | 1000.8694 | -14924.3545 | Lifetime Savings
22 | -15945.408 | 0.16672 | 1020.8868 | -15945.408 | Lifetime Savings
23 | -16986.8825 | 0.17006 | 1041.3045 | -16986.8825 | Lifetime Savings
24 | -18049.1866 | 0.17346 | 1062.1306 | -18049.1866 | Lifetime Savings
25 | -19132.7367 | 0.17693 | 1083.3732 | -19132.7367 | Lifetime Savings
|  |  | Total Savings | 19129.2134

## 500kVA (hidden)
Rating | 500kVA
Wilson e1 ECO Tier 1 |  |  |  | Wilson e2 ECO Amorphous Tier 2
Basic Ex works price in £s |  | 9481 |  | Basic Ex works price in £s | 12545
No Load Loss in Watts (NLL) |  | 510 |  | No Load Loss in Watts (NLL) | 300
Load Loss in Watts (LL) |  | 5500 |  | Load Loss in Watts (LL) | 3900
Additional investment in Wilson e2 ECO Amorphous Super Low Loss in £s |  |  |  |  | 3064
NLL Saved Watts | LL Saved Watts | Annual Savings
|  | Due to No Load Losses | Considering Load factor of (xx)% | Total kWh | CO2 Reduced (t)
|  |  | 70 |  | (GEF=0.537)
210 | 1600 | 1839.6 | 6867.84 | 8707.44 | 4.6759
No of Years | Extra Investment on Wilson e2 | Energy Cost in £s (per kWh) (Increasing 2.0% per annum) | Cost of energy saved for kWh/year | Extra Investment carried forward | Remarks
0 | 3064
1 | 2106.0716 | 0.11 | 957.8184 | 2106.0716 | Payback Period
2 | 1128.9846 | 0.1122 | 976.9748 | 1128.9846 | Payback Period
3 | 132.3559 | 0.11444 | 996.5143 | 132.3559 | Payback Period
4 | -884.2054 | 0.11673 | 1016.4445 | -884.2054 | Lifetime Savings
5 | -1921.0979 | 0.11907 | 1036.7734 | -1921.0979 | Lifetime Savings
6 | -2978.7282 | 0.12145 | 1057.5089 | -2978.7282 | Lifetime Savings
7 | -4057.5112 | 0.12388 | 1078.6591 | -4057.5112 | Lifetime Savings
8 | -5157.8698 | 0.12636 | 1100.2323 | -5157.8698 | Lifetime Savings
9 | -6280.2356 | 0.12888 | 1122.2369 | -6280.2356 | Lifetime Savings
10 | -7425.0487 | 0.13146 | 1144.6817 | -7425.0487 | Lifetime Savings
11 | -8592.7581 | 0.13409 | 1167.5753 | -8592.7581 | Lifetime Savings
12 | -9783.8217 | 0.13677 | 1190.9268 | -9783.8217 | Lifetime Savings
13 | -10998.7065 | 0.13951 | 1214.7453 | -10998.7065 | Lifetime Savings
14 | -12237.889 | 0.1423 | 1239.0402 | -12237.889 | Lifetime Savings
15 | -13501.8552 | 0.14514 | 1263.821 | -13501.8552 | Lifetime Savings
16 | -14791.1007 | 0.14805 | 1289.0975 | -14791.1007 | Lifetime Savings
17 | -16106.1311 | 0.15101 | 1314.8794 | -16106.1311 | Lifetime Savings
18 | -17447.4621 | 0.15403 | 1341.177 | -17447.4621 | Lifetime Savings
19 | -18815.6198 | 0.15711 | 1368.0005 | -18815.6198 | Lifetime Savings
20 | -20211.1406 | 0.16025 | 1395.3605 | -20211.1406 | Lifetime Savings
21 | -21634.5718 | 0.16345 | 1423.2678 | -21634.5718 | Lifetime Savings
22 | -23086.4716 | 0.16672 | 1451.7331 | -23086.4716 | Lifetime Savings
23 | -24567.4095 | 0.17006 | 1480.7678 | -24567.4095 | Lifetime Savings
24 | -26077.966 | 0.17346 | 1510.3831 | -26077.966 | Lifetime Savings
25 | -27618.7338 | 0.17693 | 1540.5908 | -27618.7338 | Lifetime Savings
|  |  | Total Savings | 27615.2104

## 800kVA (hidden)
Rating | 800kVA
Wilson e1 ECO Tier 1 |  |  |  | Wilson e2 ECO Amorphous Tier 2
Basic Ex works price in £s |  | 11630 |  | Basic Ex works price in £s | 16115
No Load Loss in Watts (NLL) |  | 650 |  | No Load Loss in Watts (NLL) | 425
Load Loss in Watts (LL) |  | 8400 |  | Load Loss in Watts (LL) | 6000
Additional investment in Wilson e2 ECO Amorphous Super Low Loss in £s |  |  |  |  | 4485
NLL Saved Watts | LL Saved Watts | Annual Savings
|  | Due to No Load Losses | Considering Load factor of (xx)% | Total kWh | CO2 Reduced (t)
|  |  | 70 |  | (GEF=0.537)
225 | 2400 | 1971 | 10301.76 | 12272.76 | 6.5905
No of Years | Extra Investment on Wilson e2 | Energy Cost in £s (per kWh) (Increasing 2.0% per annum) | Cost of energy saved for kWh/year | Extra Investment carried forward | Remarks
0 | 4485
1 | 3134.8864 | 0.11 | 1350.0036 | 3134.8864 | Payback Period
2 | 1757.7705 | 0.1122 | 1377.0037 | 1757.7705 | Payback Period
3 | 353.1123 | 0.11444 | 1404.5437 | 353.1123 | Payback Period
4 | -1079.639 | 0.11673 | 1432.6346 | -1079.639 | Lifetime Savings
5 | -2541.0454 | 0.11907 | 1461.2873 | -2541.0454 | Lifetime Savings
6 | -4031.6799 | 0.12145 | 1490.5131 | -4031.6799 | Lifetime Savings
7 | -5552.1271 | 0.12388 | 1520.3233 | -5552.1271 | Lifetime Savings
8 | -7102.9832 | 0.12636 | 1550.7298 | -7102.9832 | Lifetime Savings
9 | -8684.8565 | 0.12888 | 1581.7444 | -8684.8565 | Lifetime Savings
10 | -10298.3672 | 0.13146 | 1613.3793 | -10298.3672 | Lifetime Savings
11 | -11944.1482 | 0.13409 | 1645.6469 | -11944.1482 | Lifetime Savings
12 | -13622.8447 | 0.13677 | 1678.5598 | -13622.8447 | Lifetime Savings
13 | -15335.1152 | 0.13951 | 1712.131 | -15335.1152 | Lifetime Savings
14 | -17081.6311 | 0.1423 | 1746.3736 | -17081.6311 | Lifetime Savings
15 | -18863.0774 | 0.14514 | 1781.3011 | -18863.0774 | Lifetime Savings
16 | -20680.1525 | 0.14805 | 1816.9271 | -20680.1525 | Lifetime Savings
17 | -22533.5692 | 0.15101 | 1853.2656 | -22533.5692 | Lifetime Savings
18 | -24424.0542 | 0.15403 | 1890.331 | -24424.0542 | Lifetime Savings
19 | -26352.3488 | 0.15711 | 1928.1376 | -26352.3488 | Lifetime Savings
20 | -28319.2094 | 0.16025 | 1966.7003 | -28319.2094 | Lifetime Savings
21 | -30325.4072 | 0.16345 | 2006.0343 | -30325.4072 | Lifetime Savings
22 | -32371.7289 | 0.16672 | 2046.155 | -32371.7289 | Lifetime Savings
23 | -34458.9771 | 0.17006 | 2087.0781 | -34458.9771 | Lifetime Savings
24 | -36587.9703 | 0.17346 | 2128.8197 | -36587.9703 | Lifetime Savings
25 | -38759.5433 | 0.17693 | 2171.3961 | -38759.5433 | Lifetime Savings
|  |  | Total Savings | 38756.0199

## 1000kVA (hidden)
Rating | 1000KVA
Wilson e1 ECO Tier 1 |  |  |  | Wilson e2 ECO Amorphous Tier 2
Basic Ex works price in £s |  | 12545 |  | Basic Ex works price in £s | 18260
No Load Loss in Watts (NLL) |  | 770 |  | No Load Loss in Watts (NLL) | 500
Load Loss in Watts (LL) |  | 10500 |  | Load Loss in Watts (LL) | 7600
Additional investment in Wilson e2 ECO Amorphous Super Low Loss in £s |  |  |  |  | 5715
NLL Saved Watts | LL Saved Watts | Annual Savings
|  | Due to No Load Losses | Considering Load factor of (xx)% | Total kWh | CO2 Reduced (t)
|  |  | 70 |  | (GEF=0.537)
270 | 2900 | 2365.2 | 12447.96 | 14813.16 | 7.9547
No of Years | Extra Investment on Wilson e2 | Energy Cost in £s (per kWh) (Increasing 2.0% per annum) | Cost of energy saved for kWh/year | Extra Investment carried forward | Remarks
0 | 5715
1 | 4085.4424 | 0.11 | 1629.4476 | 4085.4424 | Payback Period
2 | 2423.2936 | 0.1122 | 1662.0366 | 2423.2936 | Payback Period
3 | 727.9019 | 0.11444 | 1695.2773 | 727.9019 | Payback Period
4 | -1001.3976 | 0.11673 | 1729.1828 | -1001.3976 | Lifetime Savings
5 | -2765.2832 | 0.11907 | 1763.7665 | -2765.2832 | Lifetime Savings
6 | -4564.4465 | 0.12145 | 1799.0418 | -4564.4465 | Lifetime Savings
7 | -6399.593 | 0.12388 | 1835.0227 | -6399.593 | Lifetime Savings
8 | -8271.4424 | 0.12636 | 1871.7231 | -8271.4424 | Lifetime Savings
9 | -10180.7289 | 0.12888 | 1909.1576 | -10180.7289 | Lifetime Savings
10 | -12128.2011 | 0.13146 | 1947.3407 | -12128.2011 | Lifetime Savings
11 | -14114.6227 | 0.13409 | 1986.2875 | -14114.6227 | Lifetime Savings
12 | -16140.7727 | 0.13677 | 2026.0133 | -16140.7727 | Lifetime Savings
13 | -18207.4458 | 0.13951 | 2066.5335 | -18207.4458 | Lifetime Savings
14 | -20315.4523 | 0.1423 | 2107.8642 | -20315.4523 | Lifetime Savings
15 | -22465.619 | 0.14514 | 2150.0215 | -22465.619 | Lifetime Savings
16 | -24658.7889 | 0.14805 | 2193.0219 | -24658.7889 | Lifetime Savings
17 | -26895.8223 | 0.15101 | 2236.8824 | -26895.8223 | Lifetime Savings
18 | -29177.5964 | 0.15403 | 2281.62 | -29177.5964 | Lifetime Savings
19 | -31505.0059 | 0.15711 | 2327.2524 | -31505.0059 | Lifetime Savings
20 | -33878.9636 | 0.16025 | 2373.7975 | -33878.9636 | Lifetime Savings
21 | -36300.4005 | 0.16345 | 2421.2734 | -36300.4005 | Lifetime Savings
22 | -38770.2661 | 0.16672 | 2469.6989 | -38770.2661 | Lifetime Savings
23 | -41289.529 | 0.17006 | 2519.0929 | -41289.529 | Lifetime Savings
24 | -43859.1772 | 0.17346 | 2569.4747 | -43859.1772 | Lifetime Savings
25 | -46480.2183 | 0.17693 | 2620.8642 | -46480.2183 | Lifetime Savings
|  |  | Total Savings | 46476.695

## 1250kVA (hidden)
Rating | 1250KVA
Wilson e1 ECO Tier 1 |  |  |  | Wilson e2 ECO Amorphous Tier 2
Basic Ex works price in £s |  | 14995 |  | Basic Ex works price in £s | 18970
No Load Loss in Watts (NLL) |  | 950 |  | No Load Loss in Watts (NLL) | 550
Load Loss in Watts (LL) |  | 11000 |  | Load Loss in Watts (LL) | 9500
Additional investment in Wilson e2 ECO Amorphous Super Low Loss in £s |  |  |  |  | 3975
NLL Saved Watts | LL Saved Watts | Annual Savings
|  | Due to No Load Losses | Considering Load factor of (xx)% | Total kWh | CO2 Reduced (t)
|  |  | 70 |  | (GEF=0.537)
400 | 1500 | 3504 | 6438.6 | 9942.6 | 5.3392
No of Years | Extra Investment on Wilson e2 | Energy Cost in £s (per kWh) (Increasing 2.0% per annum) | Cost of energy saved for kWh/year | Extra Investment carried forward | Remarks
0 | 3975
1 | 2881.204 | 0.11 | 1093.686 | 2881.204 | Payback Period
2 | 1765.5321 | 0.1122 | 1115.5597 | 1765.5321 | Payback Period
3 | 627.5467 | 0.11444 | 1137.8709 | 627.5467 | Payback Period
4 | -533.1983 | 0.11673 | 1160.6283 | -533.1983 | Lifetime Savings
5 | -1717.1583 | 0.11907 | 1183.8409 | -1717.1583 | Lifetime Savings
6 | -2924.7975 | 0.12145 | 1207.5177 | -2924.7975 | Lifetime Savings
7 | -4156.5894 | 0.12388 | 1231.6681 | -4156.5894 | Lifetime Savings
8 | -5413.0172 | 0.12636 | 1256.3014 | -5413.0172 | Lifetime Savings
9 | -6694.5736 | 0.12888 | 1281.4275 | -6694.5736 | Lifetime Savings
10 | -8001.761 | 0.13146 | 1307.056 | -8001.761 | Lifetime Savings
11 | -9335.0923 | 0.13409 | 1333.1971 | -9335.0923 | Lifetime Savings
12 | -10695.0901 | 0.13677 | 1359.8611 | -10695.0901 | Lifetime Savings
13 | -12082.2879 | 0.13951 | 1387.0583 | -12082.2879 | Lifetime Savings
14 | -13497.2297 | 0.1423 | 1414.7995 | -13497.2297 | Lifetime Savings
15 | -14940.4702 | 0.14514 | 1443.0955 | -14940.4702 | Lifetime Savings
16 | -16412.5757 | 0.14805 | 1471.9574 | -16412.5757 | Lifetime Savings
17 | -17914.1232 | 0.15101 | 1501.3965 | -17914.1232 | Lifetime Savings
18 | -19445.7016 | 0.15403 | 1531.4244 | -19445.7016 | Lifetime Savings
19 | -21007.9117 | 0.15711 | 1562.0529 | -21007.9117 | Lifetime Savings
20 | -22601.3659 | 0.16025 | 1593.294 | -22601.3659 | Lifetime Savings
21 | -24226.6892 | 0.16345 | 1625.1599 | -24226.6892 | Lifetime Savings
22 | -25884.519 | 0.16672 | 1657.6631 | -25884.519 | Lifetime Savings
23 | -27575.5054 | 0.17006 | 1690.8163 | -27575.5054 | Lifetime Savings
24 | -29300.3115 | 0.17346 | 1724.6326 | -29300.3115 | Lifetime Savings
25 | -31059.6137 | 0.17693 | 1759.1253 | -31059.6137 | Lifetime Savings
|  |  | Total Savings | 31056.0904

## 1500kVA (hidden)
Rating | 1500kVA
Wilson e1 ECO Tier 1 |  |  |  | Wilson e2 ECO Amorphous Tier 2
Basic Ex works price in £s |  | 17240 |  | Basic Ex works price in £s | 22150
No Load Loss in Watts (NLL) |  | 1125 |  | No Load Loss in Watts (NLL) | 625
Load Loss in Watts (LL) |  | 13140 |  | Load Loss in Watts (LL) | 11285
Additional investment in Wilson e2 ECO Amorphous Super Low Loss in £s |  |  |  |  | 4910
NLL Saved Watts | LL Saved Watts | Annual Savings
|  | Due to No Load Losses | Considering Load factor of (xx)% | Total kWh | CO2 Reduced (t)
|  |  | 70 |  | (GEF=0.537)
500 | 1855 | 4380 | 7962.402 | 12342.402 | 6.6279
No of Years | Extra Investment on Wilson e2 | Energy Cost in £s (per kWh) (Increasing 2.0% per annum) | Cost of energy saved for kWh/year | Extra Investment carried forward | Remarks
0 | 4910
1 | 3552.2258 | 0.11 | 1357.6642 | 3552.2258 | Payback Period
2 | 2167.2961 | 0.1122 | 1384.8175 | 2167.2961 | Payback Period
3 | 754.6678 | 0.11444 | 1412.5139 | 754.6678 | Payback Period
4 | -686.2131 | 0.11673 | 1440.7641 | -686.2131 | Lifetime Savings
5 | -2155.9116 | 0.11907 | 1469.5794 | -2155.9116 | Lifetime Savings
6 | -3655.004 | 0.12145 | 1498.971 | -3655.004 | Lifetime Savings
7 | -5184.0783 | 0.12388 | 1528.9504 | -5184.0783 | Lifetime Savings
8 | -6743.7341 | 0.12636 | 1559.5294 | -6743.7341 | Lifetime Savings
9 | -8334.583 | 0.12888 | 1590.72 | -8334.583 | Lifetime Savings
10 | -9957.2489 | 0.13146 | 1622.5344 | -9957.2489 | Lifetime Savings
11 | -11612.3681 | 0.13409 | 1654.9851 | -11612.3681 | Lifetime Savings
12 | -13300.5897 | 0.13677 | 1688.0848 | -13300.5897 | Lifetime Savings
13 | -15022.5757 | 0.13951 | 1721.8465 | -15022.5757 | Lifetime Savings
14 | -16779.0014 | 0.1423 | 1756.2834 | -16779.0014 | Lifetime Savings
15 | -18570.5557 | 0.14514 | 1791.4091 | -18570.5557 | Lifetime Savings
16 | -20397.941 | 0.14805 | 1827.2373 | -20397.941 | Lifetime Savings
17 | -22261.874 | 0.15101 | 1863.782 | -22261.874 | Lifetime Savings
18 | -24163.0857 | 0.15403 | 1901.0577 | -24163.0857 | Lifetime Savings
19 | -26102.3217 | 0.15711 | 1939.0788 | -26102.3217 | Lifetime Savings
20 | -28080.3423 | 0.16025 | 1977.8604 | -28080.3423 | Lifetime Savings
21 | -30097.9234 | 0.16345 | 2017.4176 | -30097.9234 | Lifetime Savings
22 | -32155.8561 | 0.16672 | 2057.766 | -32155.8561 | Lifetime Savings
23 | -34254.9474 | 0.17006 | 2098.9213 | -34254.9474 | Lifetime Savings
24 | -36396.0206 | 0.17346 | 2140.8997 | -36396.0206 | Lifetime Savings
25 | -38579.9152 | 0.17693 | 2183.7177 | -38579.9152 | Lifetime Savings
|  |  | Total Savings | 38576.3919

## 2000kVA (hidden)
Rating | 2000kVA
Wilson e1 ECO Tier 1 |  |  |  | Wilson e2 ECO Amorphous Tier 2
Basic Ex works price in £s |  | 21115 |  | Basic Ex works price in £s | 28355
No Load Loss in Watts (NLL) |  | 1450 |  | No Load Loss in Watts (NLL) | 850
Load Loss in Watts (LL) |  | 18000 |  | Load Loss in Watts (LL) | 15000
Additional investment in Wilson e2 ECO Amorphous Super Low Loss in £s |  |  |  |  | 7240
NLL Saved Watts | LL Saved Watts | Annual Savings
|  | Due to No Load Losses | Considering Load factor of (xx)% | Total kWh | CO2 Reduced (t)
|  |  | 70 |  | (GEF=0.537)
600 | 3000 | 5256 | 12877.2 | 18133.2 | 9.7375
No of Years | Extra Investment on Wilson e2 | Energy Cost in £s (per kWh) (Increasing 2.0% per annum) | Cost of energy saved for kWh/year | Extra Investment carried forward | Remarks
0 | 7240
1 | 5245.238 | 0.11 | 1994.652 | 5245.238 | Payback Period
2 | 3210.5808 | 0.1122 | 2034.545 | 3210.5808 | Payback Period
3 | 1135.2304 | 0.11444 | 2075.2359 | 1135.2304 | Payback Period
4 | -981.627 | 0.11673 | 2116.7407 | -981.627 | Lifetime Savings
5 | -3140.8216 | 0.11907 | 2159.0755 | -3140.8216 | Lifetime Savings
6 | -5343.2 | 0.12145 | 2202.257 | -5343.2 | Lifetime Savings
7 | -7589.626 | 0.12388 | 2246.3021 | -7589.626 | Lifetime Savings
8 | -9880.9805 | 0.12636 | 2291.2282 | -9880.9805 | Lifetime Savings
9 | -12218.1621 | 0.12888 | 2337.0527 | -12218.1621 | Lifetime Savings
10 | -14602.0874 | 0.13146 | 2383.7938 | -14602.0874 | Lifetime Savings
11 | -17033.6911 | 0.13409 | 2431.4697 | -17033.6911 | Lifetime Savings
12 | -19513.9269 | 0.13677 | 2480.0991 | -19513.9269 | Lifetime Savings
13 | -22043.7675 | 0.13951 | 2529.701 | -22043.7675 | Lifetime Savings
14 | -24624.2048 | 0.1423 | 2580.2951 | -24624.2048 | Lifetime Savings
15 | -27256.2509 | 0.14514 | 2631.901 | -27256.2509 | Lifetime Savings
16 | -29940.9379 | 0.14805 | 2684.539 | -29940.9379 | Lifetime Savings
17 | -32679.3187 | 0.15101 | 2738.2298 | -32679.3187 | Lifetime Savings
18 | -35472.4671 | 0.15403 | 2792.9943 | -35472.4671 | Lifetime Savings
19 | -38321.4784 | 0.15711 | 2848.8542 | -38321.4784 | Lifetime Savings
20 | -41227.47 | 0.16025 | 2905.8313 | -41227.47 | Lifetime Savings
21 | -44191.5814 | 0.16345 | 2963.9479 | -44191.5814 | Lifetime Savings
22 | -47214.975 | 0.16672 | 3023.2269 | -47214.975 | Lifetime Savings
23 | -50298.8365 | 0.17006 | 3083.6914 | -50298.8365 | Lifetime Savings
24 | -53444.3752 | 0.17346 | 3145.3653 | -53444.3752 | Lifetime Savings
25 | -56652.8247 | 0.17693 | 3208.2726 | -56652.8247 | Lifetime Savings
|  |  | Total Savings | 56649.3014

## 2500kVA (hidden)
Rating | 2500kVA
Wilson e1 ECO Tier 1 |  |  |  | Wilson e2 ECO Amorphous Tier 2
Basic Ex works price in £s |  | 25400 |  | Basic Ex works price in £s | 32130
No Load Loss in Watts (NLL) |  | 1750 |  | No Load Loss in Watts (NLL) | 900
Load Loss in Watts (LL) |  | 22000 |  | Load Loss in Watts (LL) | 18500
Additional investment in Wilson e2 ECO Amorphous Super Low Loss in £s |  |  |  |  | 6730
NLL Saved Watts | LL Saved Watts | Annual Savings
|  | Due to No Load Losses | Considering Load factor of (xx)% | Total kWh | CO2 Reduced (t)
|  |  | 80 |  | (GEF=0.537)
850 | 3500 | 7446 | 19622.4 | 27068.4 | 14.5357
No of Years | Extra Investment on Wilson e2 | Energy Cost in £s (per kWh) (Increasing 2.0% per annum) | Cost of energy saved for kWh/year | Extra Investment carried forward | Remarks
0 | 6730
1 | 3752.366 | 0.11 | 2977.524 | 3752.366 | Payback Period
2 | 715.1793 | 0.1122 | 3037.0745 | 715.1793 | Payback Period
3 | -2382.7511 | 0.11444 | 3097.816 | -2382.7511 | Lifetime Savings
4 | -5542.6401 | 0.11673 | 3159.7723 | -5542.6401 | Lifetime Savings
5 | -8765.7269 | 0.11907 | 3222.9677 | -8765.7269 | Lifetime Savings
6 | -12053.2755 | 0.12145 | 3287.4271 | -12053.2755 | Lifetime Savings
7 | -15406.575 | 0.12388 | 3353.1756 | -15406.575 | Lifetime Savings
8 | -18826.9405 | 0.12636 | 3420.2391 | -18826.9405 | Lifetime Savings
9 | -22315.7133 | 0.12888 | 3488.6439 | -22315.7133 | Lifetime Savings
10 | -25874.2615 | 0.13146 | 3558.4168 | -25874.2615 | Lifetime Savings
11 | -29503.9808 | 0.13409 | 3629.5851 | -29503.9808 | Lifetime Savings
12 | -33206.2944 | 0.13677 | 3702.1768 | -33206.2944 | Lifetime Savings
13 | -36982.6543 | 0.13951 | 3776.2204 | -36982.6543 | Lifetime Savings
14 | -40834.5414 | 0.1423 | 3851.7448 | -40834.5414 | Lifetime Savings
15 | -44763.4662 | 0.14514 | 3928.7797 | -44763.4662 | Lifetime Savings
16 | -48770.9695 | 0.14805 | 4007.3553 | -48770.9695 | Lifetime Savings
17 | -52858.6229 | 0.15101 | 4087.5024 | -52858.6229 | Lifetime Savings
18 | -57028.0294 | 0.15403 | 4169.2524 | -57028.0294 | Lifetime Savings
19 | -61280.8239 | 0.15711 | 4252.6375 | -61280.8239 | Lifetime Savings
20 | -65618.6744 | 0.16025 | 4337.6902 | -65618.6744 | Lifetime Savings
21 | -70043.2819 | 0.16345 | 4424.444 | -70043.2819 | Lifetime Savings
22 | -74556.3816 | 0.16672 | 4512.9329 | -74556.3816 | Lifetime Savings
23 | -79159.7432 | 0.17006 | 4603.1916 | -79159.7432 | Lifetime Savings
24 | -83855.172 | 0.17346 | 4695.2554 | -83855.172 | Lifetime Savings
25 | -88644.5095 | 0.17693 | 4789.1605 | -88644.5095 | Lifetime Savings
|  |  | Total Savings | 88640.9862

## Replacement TX - e2 Losses Calc
Rating | 1600 |  |  | TX Type | pre 2015
Standard CRGO Transformer |  |  |  | Wilson e2 ECO Amorphous Tier 2
Basic Ex works price in £s |  | 0 |  | Basic Ex works price in £s | 23155
No Load Loss in Watts (NLL) |  | 1800 |  | No Load Loss in Watts (NLL) | 630
Load Loss in Watts (LL) |  | 21700 |  | Load Loss in Watts (LL) | 12000
Additional investment in Wilson e2 ECO Amorphous Super Low Loss in £s |  |  |  |  | 23155
Data only available for 500 & 1000kVA |  | Annual Savings
|  | Due to No Load Losses | Considering Load factor of (xx)% | Total kWh | CO2 Reduced (t)
NLL Saved Watts | LL Saved Watts |  | 70 |  | (GEF=0.283)
1170 | 9700 | 10249.2 | 41636.28 | 51885.48 | 14.6836
No of Years | Extra Investment on Wilson e2 | Energy Cost in £s (per kWh) (Increasing 2.0% per annum) | Cost of energy saved for kWh/year | Extra Investment carried forward | Remarks
0 | 23155
1 | 17447.4872 | 0.11 | 5707.4028 | 17447.4872 | Payback Period
2 | 11625.8241 | 0.1122 | 5821.5509 | 11625.8241 | Payback Period
3 | 5687.7278 | 0.11444 | 5937.9819 | 5687.7278 | Payback Period
4 | -369.1304 | 0.11673 | 6056.7415 | -369.1304 | Lifetime Savings
5 | -6547.1258 | 0.11907 | 6177.8763 | -6547.1258 | Lifetime Savings
6 | -12848.6811 | 0.12145 | 6301.4339 | -12848.6811 | Lifetime Savings
7 | -19276.2676 | 0.12388 | 6427.4625 | -19276.2676 | Lifetime Savings
8 | -25832.4057 | 0.12636 | 6556.0118 | -25832.4057 | Lifetime Savings
9 | -32519.6666 | 0.12888 | 6687.132 | -32519.6666 | Lifetime Savings
10 | -39340.6728 | 0.13146 | 6820.8747 | -39340.6728 | Lifetime Savings
11 | -46298.099 | 0.13409 | 6957.2922 | -46298.099 | Lifetime Savings
12 | -53394.6738 | 0.13677 | 7096.438 | -53394.6738 | Lifetime Savings
13 | -60633.1801 | 0.13951 | 7238.3668 | -60633.1801 | Lifetime Savings
14 | -68016.4565 | 0.1423 | 7383.1341 | -68016.4565 | Lifetime Savings
15 | -75547.3984 | 0.14514 | 7530.7968 | -75547.3984 | Lifetime Savings
16 | -83228.9592 | 0.14805 | 7681.4127 | -83228.9592 | Lifetime Savings
17 | -91064.1512 | 0.15101 | 7835.041 | -91064.1512 | Lifetime Savings
18 | -99056.047 | 0.15403 | 7991.7418 | -99056.047 | Lifetime Savings
19 | -107207.7807 | 0.15711 | 8151.5766 | -107207.7807 | Lifetime Savings
20 | -115522.5491 | 0.16025 | 8314.6082 | -115522.5491 | Lifetime Savings
21 | -124003.6129 | 0.16345 | 8480.9003 | -124003.6129 | Lifetime Savings
22 | -132654.298 | 0.16672 | 8650.5183 | -132654.298 | Lifetime Savings
23 | -141477.9967 | 0.17006 | 8823.5287 | -141477.9967 | Lifetime Savings
24 | -150478.1695 | 0.17346 | 8999.9993 | -150478.1695 | Lifetime Savings
25 | -159658.3457 | 0.17693 | 9179.9993 | -159658.3457 | Lifetime Savings
26 | -169022.1254 | 0.18047 | 9363.5992 | -169022.1254 | Lifetime Savings
27 | -178573.1807 | 0.18408 | 9550.8712 | -178573.1807 | Lifetime Savings
28 | -188315.2571 | 0.18776 | 9741.8887 | -188315.2571 | Lifetime Savings
29 | -198252.175 | 0.19151 | 9936.7264 | -198252.175 | Lifetime Savings
30 | -208387.8313 | 0.19534 | 10135.461 | -208387.8313 | Lifetime Savings
|  |  | Total Savings | 208383.3688

## New Build - Losses Calc e1-e2
Rating | 1600 |  |  | Compare to: | Wilson e1
Wilson e1 ECO CRGO Tier 1 |  |  |  | Wilson e2 ECO Amorphous Tier 2
Basic Ex works price in £s |  | 18155 |  | Basic Ex works price in £s | 23155
No Load Loss in Watts (NLL) |  | 1200 |  | No Load Loss in Watts (NLL) | 630
Load Loss in Watts (LL) |  | 14000 |  | Load Loss in Watts (LL) | 12000
Additional investment in Wilson e2 ECO Amorphous Super Low Loss in £s |  |  |  |  | 5000
Data only available for 500 & 1000kVA |  | Annual Savings
|  | Due to No Load Losses | Considering Load factor of (xx)% | Total kWh | CO2 Reduced (t)
NLL Saved Watts | LL Saved Watts |  | 70 |  | (GEF=0.283)
570 | 2000 | 4993.2 | 8584.8 | 13578 | 3.8426
No of Years | Extra Investment on Wilson e2 | Energy Cost in £s (per kWh) (Increasing 2.0% per annum) | Cost of energy saved for kWh/year | Extra Investment carried forward | Remarks
0 | 5000
1 | 3506.31 | 0.11 | 1493.58 | 3506.31 | Payback Period
2 | 1982.7462 | 0.1122 | 1523.4516 | 1982.7462 | Payback Period
3 | 428.7111 | 0.11444 | 1553.9206 | 428.7111 | Payback Period
4 | -1156.4047 | 0.11673 | 1584.999 | -1156.4047 | Lifetime Savings
5 | -2773.2227 | 0.11907 | 1616.699 | -2773.2227 | Lifetime Savings
6 | -4422.3772 | 0.12145 | 1649.033 | -4422.3772 | Lifetime Savings
7 | -6104.5147 | 0.12388 | 1682.0137 | -6104.5147 | Lifetime Savings
8 | -7820.295 | 0.12636 | 1715.6539 | -7820.295 | Lifetime Savings
9 | -9570.3909 | 0.12888 | 1749.967 | -9570.3909 | Lifetime Savings
10 | -11355.4888 | 0.13146 | 1784.9664 | -11355.4888 | Lifetime Savings
11 | -13176.2885 | 0.13409 | 1820.6657 | -13176.2885 | Lifetime Savings
12 | -15033.5043 | 0.13677 | 1857.079 | -15033.5043 | Lifetime Savings
13 | -16927.8644 | 0.13951 | 1894.2206 | -16927.8644 | Lifetime Savings
14 | -18860.1117 | 0.1423 | 1932.105 | -18860.1117 | Lifetime Savings
15 | -20831.0039 | 0.14514 | 1970.7471 | -20831.0039 | Lifetime Savings
16 | -22841.314 | 0.14805 | 2010.162 | -22841.314 | Lifetime Savings
17 | -24891.8303 | 0.15101 | 2050.3653 | -24891.8303 | Lifetime Savings
18 | -26983.3569 | 0.15403 | 2091.3726 | -26983.3569 | Lifetime Savings
19 | -29116.714 | 0.15711 | 2133.2 | -29116.714 | Lifetime Savings
20 | -31292.7383 | 0.16025 | 2175.864 | -31292.7383 | Lifetime Savings
21 | -33512.2831 | 0.16345 | 2219.3813 | -33512.2831 | Lifetime Savings
22 | -35776.2187 | 0.16672 | 2263.7689 | -35776.2187 | Lifetime Savings
23 | -38085.4331 | 0.17006 | 2309.0443 | -38085.4331 | Lifetime Savings
24 | -40440.8318 | 0.17346 | 2355.2252 | -40440.8318 | Lifetime Savings
25 | -42843.3384 | 0.17693 | 2402.3297 | -42843.3384 | Lifetime Savings
26 | -45293.8952 | 0.18047 | 2450.3763 | -45293.8952 | Lifetime Savings
27 | -47793.4631 | 0.18408 | 2499.3838 | -47793.4631 | Lifetime Savings
28 | -50343.0223 | 0.18776 | 2549.3715 | -50343.0223 | Lifetime Savings
29 | -52943.5728 | 0.19151 | 2600.3589 | -52943.5728 | Lifetime Savings
30 | -55596.1342 | 0.19534 | 2652.3661 | -55596.1342 | Lifetime Savings
|  |  | Total Savings | 55591.6717

## Replacement TX - e3 Losses Calc
Rating | 1000 |  |  | TX Type | pre 2015
Standard CRGO Transformer |  |  |  | Wilson e3 ECO Amorphous
Basic Ex works price in £s |  | 0 |  | Basic Ex works price in £s | 20750
No Load Loss in Watts (NLL) |  | 1350 |  | No Load Loss in Watts (NLL) | 450
Load Loss in Watts (LL) |  | 12500 |  | Load Loss in Watts (LL) | 6840
Additional investment in Wilson e2 ECO Amorphous Super Low Loss in £s |  |  |  |  | 20750
Data only available for 500 & 1000kVA |  | Annual Savings
|  | Due to No Load Losses | Considering Load factor of (xx)% | Total kWh | CO2 Reduced (t)
NLL Saved Watts | LL Saved Watts |  | 70 |  | (GEF=0.283)
900 | 5660 | 7884 | 24294.984 | 32178.984 | 9.1067
No of Years | Extra Investment on Wilson e2 | Energy Cost in £s (per kWh) (Increasing 2.0% per annum) | Cost of energy saved for kWh/year | Extra Investment carried forward | Remarks
0 | 20750
1 | 17210.2018 | 0.11 | 3539.6882 | 17210.2018 | Payback Period
2 | 13599.6076 | 0.1122 | 3610.482 | 13599.6076 | Payback Period
3 | 9916.8015 | 0.11444 | 3682.6916 | 9916.8015 | Payback Period
4 | 6160.3393 | 0.11673 | 3756.3455 | 6160.3393 | Payback Period
5 | 2328.7478 | 0.11907 | 3831.4724 | 2328.7478 | Payback Period
6 | -1579.4755 | 0.12145 | 3908.1018 | -1579.4755 | Lifetime Savings
7 | -5565.8632 | 0.12388 | 3986.2639 | -5565.8632 | Lifetime Savings
8 | -9631.9787 | 0.12636 | 4065.9891 | -9631.9787 | Lifetime Savings
9 | -13779.4166 | 0.12888 | 4147.3089 | -13779.4166 | Lifetime Savings
10 | -18009.8031 | 0.13146 | 4230.2551 | -18009.8031 | Lifetime Savings
11 | -22324.7974 | 0.13409 | 4314.8602 | -22324.7974 | Lifetime Savings
12 | -26726.0916 | 0.13677 | 4401.1574 | -26726.0916 | Lifetime Savings
13 | -31215.4117 | 0.13951 | 4489.1806 | -31215.4117 | Lifetime Savings
14 | -35794.5182 | 0.1423 | 4578.9642 | -35794.5182 | Lifetime Savings
15 | -40465.2068 | 0.14514 | 4670.5435 | -40465.2068 | Lifetime Savings
16 | -45229.3091 | 0.14805 | 4763.9543 | -45229.3091 | Lifetime Savings
17 | -50088.6936 | 0.15101 | 4859.2334 | -50088.6936 | Lifetime Savings
18 | -55045.2657 | 0.15403 | 4956.4181 | -55045.2657 | Lifetime Savings
19 | -60100.9692 | 0.15711 | 5055.5464 | -60100.9692 | Lifetime Savings
20 | -65257.7869 | 0.16025 | 5156.6574 | -65257.7869 | Lifetime Savings
21 | -70517.7408 | 0.16345 | 5259.7905 | -70517.7408 | Lifetime Savings
22 | -75882.8939 | 0.16672 | 5364.9863 | -75882.8939 | Lifetime Savings
23 | -81355.35 | 0.17006 | 5472.2861 | -81355.35 | Lifetime Savings
24 | -86937.2552 | 0.17346 | 5581.7318 | -86937.2552 | Lifetime Savings
25 | -92630.7986 | 0.17693 | 5693.3664 | -92630.7986 | Lifetime Savings
26 | -98438.2128 | 0.18047 | 5807.2337 | -98438.2128 | Lifetime Savings
27 | -104361.7753 | 0.18408 | 5923.3784 | -104361.7753 | Lifetime Savings
28 | -110403.809 | 0.18776 | 6041.846 | -110403.809 | Lifetime Savings
29 | -116566.6835 | 0.19151 | 6162.6829 | -116566.6835 | Lifetime Savings
30 | -122852.8154 | 0.19534 | 6285.9366 | -122852.8154 | Lifetime Savings
|  |  | Total Savings | 122848.3529

## New Build - Losses Calc e1-e3
Rating | 1000 |  |  | Compare to: | Wilson e1
Wilson e1 ECO CRGO Tier 1 |  |  |  | Wilson e3 ECO Amorphous
Basic Ex works price in £s |  | 12545 |  | Basic Ex works price in £s | 20750
No Load Loss in Watts (NLL) |  | 770 |  | No Load Loss in Watts (NLL) | 450
Load Loss in Watts (LL) |  | 10500 |  | Load Loss in Watts (LL) | 6840
Additional investment in Wilson e2 ECO Amorphous Super Low Loss in £s |  |  |  |  | 8205
Data only available for 500 & 1000kVA |  | Annual Savings
|  | Due to No Load Losses | Considering Load factor of (xx)% | Total kWh | CO2 Reduced (t)
NLL Saved Watts | LL Saved Watts |  | 70 |  | (GEF=0.283)
320 | 3660 | 2803.2 | 15710.184 | 18513.384 | 5.2393
No of Years | Extra Investment on Wilson e2 | Energy Cost in £s (per kWh) (Increasing 2.0% per annum) | Cost of energy saved for kWh/year | Extra Investment carried forward | Remarks
0 | 8205
1 | 6168.4178 | 0.11 | 2036.4722 | 6168.4178 | Payback Period
2 | 4091.1039 | 0.1122 | 2077.2017 | 4091.1039 | Payback Period
3 | 1972.2437 | 0.11444 | 2118.7457 | 1972.2437 | Payback Period
4 | -188.9937 | 0.11673 | 2161.1206 | -188.9937 | Lifetime Savings
5 | -2393.4558 | 0.11907 | 2204.343 | -2393.4558 | Lifetime Savings
6 | -4642.0071 | 0.12145 | 2248.4299 | -4642.0071 | Lifetime Savings
7 | -6935.5295 | 0.12388 | 2293.3985 | -6935.5295 | Lifetime Savings
8 | -9274.9223 | 0.12636 | 2339.2665 | -9274.9223 | Lifetime Savings
9 | -11661.103 | 0.12888 | 2386.0518 | -11661.103 | Lifetime Savings
10 | -14095.0073 | 0.13146 | 2433.7728 | -14095.0073 | Lifetime Savings
11 | -16577.5897 | 0.13409 | 2482.4483 | -16577.5897 | Lifetime Savings
12 | -19109.8237 | 0.13677 | 2532.0973 | -19109.8237 | Lifetime Savings
13 | -21692.7025 | 0.13951 | 2582.7392 | -21692.7025 | Lifetime Savings
14 | -24327.2387 | 0.1423 | 2634.394 | -24327.2387 | Lifetime Savings
15 | -27014.4658 | 0.14514 | 2687.0819 | -27014.4658 | Lifetime Savings
16 | -29755.4373 | 0.14805 | 2740.8235 | -29755.4373 | Lifetime Savings
17 | -32551.2283 | 0.15101 | 2795.64 | -32551.2283 | Lifetime Savings
18 | -35402.9351 | 0.15403 | 2851.5528 | -35402.9351 | Lifetime Savings
19 | -38311.6761 | 0.15711 | 2908.5838 | -38311.6761 | Lifetime Savings
20 | -41278.5918 | 0.16025 | 2966.7555 | -41278.5918 | Lifetime Savings
21 | -44304.8459 | 0.16345 | 3026.0906 | -44304.8459 | Lifetime Savings
22 | -47391.625 | 0.16672 | 3086.6124 | -47391.625 | Lifetime Savings
23 | -50540.1398 | 0.17006 | 3148.3447 | -50540.1398 | Lifetime Savings
24 | -53751.6248 | 0.17346 | 3211.3116 | -53751.6248 | Lifetime Savings
25 | -57027.3396 | 0.17693 | 3275.5378 | -57027.3396 | Lifetime Savings
26 | -60368.5686 | 0.18047 | 3341.0486 | -60368.5686 | Lifetime Savings
27 | -63776.6222 | 0.18408 | 3407.8695 | -63776.6222 | Lifetime Savings
28 | -67252.8369 | 0.18776 | 3476.0269 | -67252.8369 | Lifetime Savings
29 | -70798.5759 | 0.19151 | 3545.5475 | -70798.5759 | Lifetime Savings
30 | -74415.2296 | 0.19534 | 3616.4584 | -74415.2296 | Lifetime Savings
|  |  | Total Savings | 74410.7671

## Data
Rating | pre 2015 |  | 2015 |  | 1950's |  | 1970's |  | 1990's |  | post 2015 |  | Standard |  | 2018
| e1 |  | e2 Amorphous | [7 empty] | e1 |  | Tier 2 |  | e3 Amorphous
| Load Losses | No Load Losses | Load Losses | No Load Losses | Load Losses | No Load Losses | Load Losses | No Load Losses | Load Losses | No Load Losses | Load Losses | No Load Losses | Load Losses | No Load Losses | Load Losses | No Load Losses
315 | 5350 | 600 | 2800 | 200 | 5384.6154 | 1086 | 5584.6154 | 676 | 5684.6154 | 530 | 3900 | 360 | 2800 | 324 | 2520 | 180
500 | 7400 | 900 | 3900 | 300 | 7600 | 1660 | 7600 | 1030 | 7600 | 800 | 5500 | 510 | 3900 | 459 | 3510 | 270
800 | 11000 | 1150 | 6000 | 425 | 11846.1538 | 2395.5833 | 11417.5824 | 1481.8333 | 11203.2967 | 1140.4167 | 8400 | 650 | 6000 | 585 | 5400 | 382
1000 | 12500 | 1350 | 7000 | 500 | 14000 | 2870 | 13000 | 1770 | 12500 | 1350 | 10500 | 770 | 7600 | 693 | 6840 | 450
1250 | 16000 | 1575 | 9500 | 550 | 19243.5897 | 3213.8333 | 17207.8755 | 1976.3333 | 16190.0183 | 1494.1667 | 11000 | 950 | 9500 | 855 | 8550 | 505
1500 | 21000 | 1700 | 11285 | 625 | 23148.7179 | 3716.6667 | 19924.4322 | 2279.1667 | 18312.2894 | 1708.3333 | 13140 | 1125 |  |  | 10152 | 560
1600 | 21700 | 1800 | 12000 | 630 | 24923.0769 | 3811.5 | 20637.3626 | 2331 | 18494.5055 | 1732.5 | 14000 | 1200 | 12000 | 1080 | 10800 | 575
2000 | 24000 | 2300 | 15000 | 850 | 31538.4615 | 5230.3333 | 25109.8901 | 3190.3333 | 21895.6044 | 2351.6667 | 18000 | 1450 | 1500 | 1305 | 13500 | 750
2500 | 28000 | 3000 | 18500 | 900 | 39371.7949 | 5631 | 30121.7949 | 3426 | 25496.7949 | 2505 | 22000 | 1750 | 18500 | 1575 | 16650 | 810
Percentage Diff for extrapolation
Year List |  |  |  | 315 | 1.9231 | 5.43 | 1.9945 | 3.38 | 2.0302 | 2.65
post 2015 | Wilson e1 ECO CRGO Tier 1 |  |  | 500 | 1.9487 | 5.5333 | 1.9487 | 3.4333 | 1.9487 | 2.6667
pre 2015 | Standard CRGO Transformer |  |  | 800 | 1.9744 | 5.6367 | 1.9029 | 3.4867 | 1.8672 | 2.6833
1990's | Transformer made in the 90's |  |  | 1000 | 2 | 5.74 | 1.8571 | 3.54 | 1.7857 | 2.7 |  |  |  | 1950 | 1970 | 1990 | Pre 2015 | WPS e1 | Std Tier 2 | WPS e2 | WPS e3
1970's | Transformer made in the 70's |  |  | 1250 | 2.0256 | 5.8433 | 1.8114 | 3.5933 | 1.7042 | 2.7167 |  |  |  | 16870 | 14770 | 13850 | 13850 | 11270 | 8293 | 7600 | 7290
1950's | Transformer made in the 50's |  |  | 1500 | 2.0513 | 5.9467 | 1.7656 | 3.6467 | 1.6227 | 2.7333
|  |  |  | 1600 | 2.0769 | 6.05 | 1.7198 | 3.7 | 1.5412 | 2.75
Wilson e1 | Wilson e1 ECO CRGO Tier 1 |  |  | 2000 | 2.1026 | 6.1533 | 1.674 | 3.7533 | 1.4597 | 2.7667
STD Tier 2 | Standard Tier 2 Transformer |  |  | 2500 | 2.1282 | 6.2567 | 1.6282 | 3.8067 | 1.3782 | 2.7833
Rating | Basic ex-Works Price
| e1 | e2 | e3
315 | 7550 | 9995 | 11995
500 | 9481 | 12545 | 14950
800 | 11630 | 16115 | 18825
1000 | 12545 | 18260 | 20750
1250 | 14995 | 18970 | 23250
1500 | 17240 | 22150 | 26200
1600 | 18155 | 23155 | 27500
2000 | 21115 | 28355 | 32600
2500 | 25400 | 32130 | 37250